Air Disinfection Engineering Specifications

- 1.1 	SCOPE

- Contractor shall install UVC systems for within the HVAC Ducting.  The purpose is to provide microbial disinfection of air within the duct to prevent the spread of viruses and inhibit the growth of spores and molds. It is intended that all UVC systems be provided by a single manufacturer for all installations on this project.

- 1.2	QUALITY ASSURANCE

- The UVC system shall be ETL, CSA or UL LISTED by a nationally recognized testing lab (NRTL) per UL 1598 for Luminaries and the lamps and power supplies shall be rated for wet locations and air handler use. The entire UV fixture including lamps and wire harnesses (not just the UV ballast) must comply with Part 18 of the FCC rules and carry the appropriate FCC markings/designation from the UV fixture manufacturer.

- 1.3	DELIVERY, STORAGE AND HANDLING

- Store UVC systems in a clean dry place and protect from weather and construction traffic.  Handle UVC systems carefully to avoid damage to components.  Do not install damaged components; replace and return damaged components to equipment manufacturer.

- Comply with manufacturer’s installation instructions placement, wiring, and testing.

- Submit a list of spare bulbs, including number, type, specific systems served, etc. and turn over to OWNER at end of project and obtain written receipt for same.

- PART 2 PRODUCTS

- 2.1	UVC SYSTEM

- A. 	Manufacturer must meet the following minimum requirements.

- 1.   Acceptable Manufacturers – Triatomic Environmental, Inc. - Brand name "Fresh-Aire UV" or equal.

- B.  	Recommended UV Product Series:

- Fresh-Aire UV “ADS” series Airborne Duct Mount System.

- C.	Quality Assurance:

- All Power supplies shall be 100% tested utilizing a Hi-Pot tester for short circuit detection and the lamps shall be 100% tested for lighting and filament continuity.

- Output Verification: Ultraviolet light lamps shall be of 254nm type.  Total output per one-inch lamp length shall not be less than 10 micro W/cm2, at one meter.

- D.	Warranty:

- The power source and cables will carry a Lifetime warranty.

The high intensity UVC lamp(s) will be guaranteed for Two (2) years against manufacturing defects and provide the necessary performance for 18,000 hours of operation.

- 2.2  	DESIGN REQUIREMENTS

- It is intended that the CONTRACTOR coordinate with the HVAC equipment manufacturer and the UVC System manufacturer to select the proper system for each application to insure proper germicidal irradiation of air handling system components.

- Irradiation – UVC System bulbs are to be installed in sufficient quantity and in such an arrangement so as to provide an equal distribution of UVC energy within the duct. Intensity – The minimal UVC energy shall not be less than 10 micro W/cm2 per inch of lamp at 1 Meter.  No more than 20% loss is allowed over a 2-year period.

- # of Lamps – Based on Factory supplied sizing data, Lamps shall be typically suspended in the middle of the duct. It is also suggested that the area around the lamps inside the duct is covered in a reflective material for optimal performance. Lamps shall operate continuously, 24/7.

- Lamps – Each lamp shall have a useful life of 18,000 hours with no more than a 20% output loss at the end of the two (2) years of continuous use.  Lamps shall be hard quartz hot filament type High Output lamps.

- Mounting Hardware – Hardware should be provided to facilitate mounting of the lamps for proper irradiation.  All mounting hardware shall be constructed of aluminum, galvanized steel or as an option 304 stainless steel.

Power Supply – shall be constructed of extruded anodized aluminum with gasket and sealed for wet locations.  Power supply shall be constructed in a fashion to provide isolation of high voltage supply power from the lamp mounting location through remote tethering of lamps.  The power source shall be 110-277 volts AC, 50-60 Hz. and be able to operate reliably in indoor or outdoor environments ranging in temperature from 45F (8C) to 170F (86C) with relative humidity up to 100%.

- .  It shall be labeled “Suitable for Air Handling Use”, and “Suitable for Wet Locations”.

The Manufacturer shall supply a computer-generated sizing report for each AHU that includes the UVGI Lamp Data, Duct Data, Irradiation Data, Minimum and average Microbe Inactivation Rate, Log Inactivation for a Single Pass Application or a Six  (6) Pass Recirculation Application calculated at End of UVC Lamp Life (18,000 operating hours), on Four (4) Microorganisms, as well as an Installation Lamp Positioning graph showing the installation location for each lamp array .

Installation – Lamps shall be connected to Power Supply using UV and moisture resistant cabling and have IP67 water-proof cable connectors.   The lamp cables shall be clearly marked as follows "UVGI Ultraviolet Germicidal Lamp Cable - Protect Eyes From UV Light Rays". Manufacturer shall provide enough cabling to reach all lamps as applicable. Should additional cable length be required, the cable extension shall use watertight connections at both ends.

- 2.3	ACCESSORIES

- A.	Safety Interlocks – To protect maintenance personnel, all access panels

- and doors to the UVC assembly and/or within view of the UVC assembly

- must include mechanical interlock switches to ensure that the UVC assembly will be de-energized when any of these accesses are opened.

- Portal – At least one UVC assembly access shall be equipped with a UVC sight glass to facilitate viewing the assembly without the possibility of exceeding the Minimal Erythemal Dose which can cause severe eye irritation.

- Warning/Caution Stickers – Shall be placed on each access panel to prevent accidental eye exposure.

- 2.4. 	SPARE LAMPS

- Provide one (1) spare set of UVC lamps for each UVC system and turn over to the OWNER.

- 2.5.	DISCONNECT SWITCH

- MECHANICAL CONTRACTOR shall provide a separate disconnect switch as required by Code for installation by the ELECTRICAL CONTRACTOR on all installations.  Where and equipment service outlet is furnished by rooftop/air handler manufacturer, CONTRACTOR may utilize 120v or 230v single phase style power source and corded soft-wired kit to plug the UVC system into service outlet.  It is the MECHANICAL CONTRACTOR’S responsibility to coordinate these requirements with equipment